**Price Perforated Face Ceiling Panel Return**

**Division 23 – Heating, Ventilating, and Air Conditioning**

**Section 23 37 13 – Diffusers, Registers, and Grilles**

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

**PART 1 – GENERAL**

* 1. **Section includes**:

1. Perforated Face Ceiling Panel Return
   1. **Related Requirements**
2. Section 01 30 00 – Administrative Requirements
3. Section 01 40 00 – Quality Requirements
4. Section 01 74 21 – Construction/Demolition Waste Management and Disposal
5. Section 01 78 00 – Closeout Submittals
6. Section 01 79 00 – Demonstration and Training
   1. **Reference Standards**
7. All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.
8. ASTM 610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces
9. ASTM 714 – Test Method for Evaluating Degree of Blistering of Paints
10. ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes
11. ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments
12. ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

**1.04 Submittals**

1. See Section 01 30 00 – Administrative Requirements for submittal procedures.
2. Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.
3. Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.
4. Project Record Documents: Record actual locations of units and control components.
5. Operation and Maintenance Data: Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.
6. Warranty: Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.
7. Maintenance Materials: Furnish the following for Owner's use in maintenance of project.

**1.06 Quality Assurance**

1. Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

**1.07 Warranty**

1. See Section 01 78 00 - Closeout Submittals, for additional warranty requirements.
2. Provide 12 month manufacturer warranty from date of shipment of diffusers.

**PART 2 – PRODUCTS**

**2.01 Manufacturer**

1. Basis of Design: Price Industries, Inc.
   1. Perforated Face Return Ceiling Module: Model PFRF
2. General:
   1. The perforated face return diffuser shall be supplied to match Price Model PDF in appearance and detail, and provide non-ducted return airflow.
   2. For plenum return, non-ducted applications, the return diffuser shall be provided without a frame while maximizing free area.
   3. The extended face return diffusers shall match the extended face supply diffusers for tegular tile ceilings.

**2.02 Perforated Face Return Ceiling Module**

1. Description:
   1. Furnish and install Price model PFRF return diffusers in sizes and capacities as shown by the plans and air distribution schedule.
2. Construction:
   1. The return diffusers shall consist of a perforated air distribution face of no less than 51 percent free area.
   2. The perforated face screen construction shall be [steel] or [aluminum] construction.
   3. The diffuser face shall sit flush in the ceiling grid.
   4. [Option]: The extended face will allow the perforated face to sit 5/16 inch below the ceiling grid or flush to tegular style ceiling grid.
3. Mounting Frame:
   1. The diffuser mounting frame shall be suitable for T-bar lay-in applications.
4. Paint Specification:
   1. Paint finish shall be (**select one**):
      1. Baked-on powder coat finish.
         1. The paint film thickness shall be a minimum of 2 mils.
         2. The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.
         3. The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.
         4. The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.
         5. The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.
      2. All components shall have a custom finish in a color to match a customer supplied sample.

**PART 3 – EXECUTION**

**3.01 Examination**

1. Verify that conditions are suitable for installation.
2. Verify that field measurements are as shown on the drawings.

**3.02 Installation**

1. Install in accordance with manufacturer’s instructions.
2. See drawings for the size(s) and locations of diffusers.

**3.03 Field Quality Control**

1. See Section 01 40 00 – Quality Requirements for additional requirements.

**3.05 Cleaning**

1. See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

**3.06 Closeout Activities**

1. See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.
2. See Section 01 79 00 – Demonstration and Training for additional requirements.